## Sheet1
1st_floor type |  | flat with Hallway |  |  | 1st_floor
[5 empty] | SDB |  |  |  | ESDB
Emergency
Circuit No | Room Nane | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker | Circuit No | Room Nane | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
Circuit No 01 |  | SB3 | C6 (Light) | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 01 |  | ESB1 | C2 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | F4 (Fan) | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  |  | C4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB7 | K4 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  | ESB4 | C7 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | A2 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K6 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB8 | SS4 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  |  | Total | 80 | 0.45455 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  | K5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | Total | 280 | 1.5909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB | Circuit No 02 |  | ESB2 | F1 | 100 | 0.56818 | 2 x 1.5 rm BYM
[11 empty] | K2 | 20 | 0.11364 | 2 x 1.5 rm BYM
[11 empty] | Total | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 02 |  | SB5 | A1 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | SS1 | 100 | 0.56818 | 2 x 1.5 rm BYM |  | Circuit No 03 |  | ESB3 | K3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB6 | K7 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | SS3 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | E1 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  | ESB5 | F5 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | SS2 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  |  | Total | 220 | 1.25 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  | Total | 340 | 1.9318 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 03 |  | SB4 | C9 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB9 | C8 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | SS3 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | K8 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | A3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB10 | SS5 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | K9 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | Total | 300 | 1.7045 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 04 |  | SB2 | F3 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | C2 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | Total | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 05 |  | Sb1 | C5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | C3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | F1 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | C1 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | Total | 160 | 0.90909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB

## Sheet2
FLat without Hallway |  |  | 2nd_floor
SDB
ESDB
| Circuit No | Room Nane | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
| Circuit No 01 |  | SB3 | C6 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | F4 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | SB7 | K4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | A2 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Emergency
|  |  | SB8 | SS4 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  |  | K5 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No | Room Nane | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
[5 empty] | 280 | 1.5909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB | Circuit No 01 |  | ESB3 | K3 | 20 | 0.11364 | 2 x 1.5 rm BYM
[11 empty] | ESB4 | K6 | 20 | 0.11364 | 2 x 1.5 rm BYM
| Circuit No 02 |  | SB5 | A1 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C7 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | SS1 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  | ESB5 | F5 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  | SB6 | SS2 | 100 | 0.56818 | 2 x 1.5 rm BYM | [5 empty] | 160 | 0.90909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  |  | K7 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | E1 | 100 | 0.56818 | 2 x 1.5 rm BYM |  | Circuit No 02 |  | ESB2 | K1 | 20 | 0.11364 | 2 x 1.5 rm BYM
[5 empty] | 340 | 1.9318 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  | F2 | 100 | 0.56818 | 2 x 1.5 rm BYM
[13 empty] | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
| Circuit No 03 |  | SB4 | C9 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | SB9 | K8 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No03 |  | ESB1 | C5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | SS3 | 100 | 0.56818 | 2 x 1.5 rm BYM | [5 empty] | 20 | 0.11364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  |  | C8 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | A3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | SB10 | K9 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | SS5 | 100 | 0.56818 | 2 x 1.5 rm BYM
[5 empty] | 300 | 1.7045 | 2 x 1.5 rm BYM + 1.5 BYA EC | 5A SP MCB
| Circuit No 04 |  | SB2 | C5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | F3 | 100 | 0.56818 | 2 x 1.5 rm BYM
[5 empty] | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
| Circuit No 05 |  | SB1 | C1 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | C3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | C4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | F1 | 100 | 0.56818 | 2 x 1.5 rm BYM
|  |  |  | C2 | 20 | 0.11364 | 2 x 1.5 rm BYM
[5 empty] | 180 | 1.0227 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB

## Sheet3
Lobby
Circuit No | Room Name | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
Circuit No 01 |  | SB5 | K8 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No | Room Name | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
|  |  | K14 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 01 |  | ESDB3 | K14 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K10 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K15 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K11 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K12 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 80 | 0.45455 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  |  | 60 | 0.34091 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 02 |  | SB4 | K16 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 02 |  | ESDB1 | K6 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K13 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 20 | 0.11364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  | K7 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 60 | 0.34091 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB | Circuit No 03 |  | ESDB2 | K17 | 20 | 0.11364 | 2 x 1.5 rm BYM
[12 empty] | 20 | 0.11364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 03 |  | SB3 | K20 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 20 | 0.11364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 04 |  | SB3 | K4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K9 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K1 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 100 | 0.56818 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB

## Sheet4
| Ground_Floor |  |  | SDB
ESDB
Circuit No | Room Name | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
Circuit No 01 |  | SB9 | K9 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K30 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K7 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No | Room Name | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
|  | SB1 | K3 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 01 |  | ESB7 | K27 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K1 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  | ESB6 | K24 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K19 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 40 | 0.22727 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  | K5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K11 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 02 |  | ESB4 | K21 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 160 | 0.90909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  | ESB2 | F1 | 100 | 0.56818 | 2 x 1.5 rm BYM
[11 empty] | K10 | 20 | 0.11364 | 2 x 1.5 rm BYM
Circuit No 02 |  | SB7 | K26 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 140 | 0.79545 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  | SB6 | K25 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 40 | 0.22727 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB | Circuit No 03 |  | ESB3 | K13 | 20 | 0.11364 | 2 x 1.5 rm BYM
[11 empty] | K2 | 20 | 0.11364 | 2 x 1.5 rm BYM
Circuit No 03 |  | SB5 | K20 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K14 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K22 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  | ESB2 | K16 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 40 | 0.22727 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  | F4 | 100 | 0.56818 | 2 x 1.5 rm BYM
[11 empty] | K18 | 20 | 0.11364 | 2 x 1.5 rm BYM
Circuit No 04 |  | SB10 | K45 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 200 | 1.1364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  | K35 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K37 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 04 |  | ESB10 | C7 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K39 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K36 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K45 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K38 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K52 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K40 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  | K42 | 20 | 0.11364 | 2 x 1.5 rm BYM
[11 empty] | K34 | 20 | 0.11364 | 2 x 1.5 rm BYM
Circuit No 05 |  | SB11 | K46 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  | ESB9 | C5 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | C6 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K43 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K48 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K44 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K33 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 180 | 1.0227 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
|  |  |  | 80 | 0.45455 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
[8 empty] | Circuit No 05 |  | ESB5 | K6 | 20 | 0.11364 | 2 x 1.5 rm BYM
Circuit No 06 |  | SB4 | E1 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  |  | K8 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB3 | K17 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C3 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | F5 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  |  | K4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K15 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C1 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | SS5 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  |  | K2 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  | SB2 | F3 | 100 | 0.56818 | 2 x 1.5 rm BYM |  |  |  | ESB11 | K23 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K12 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  | ESB8 | K29 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 460 | 2.6136 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  |  | 160 | 0.90909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
Circuit No 07 |  | SB8 | K28 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 06 |  | ESB12 | C4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 20 | 0.11364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  | C9 | 20 | 0.11364 | 2 x 1.5 rm BYM
[11 empty] | K47 | 20 | 0.11364 | 2 x 1.5 rm BYM
[11 empty] | C8 | 20 | 0.11364 | 2 x 1.5 rm BYM
[12 empty] | 80 | 0.45455 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB

## Sheet5
Basement
Circuit No | Room Name | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
Circuit No 01 |  | SB3 | K22 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | K42 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No | Room Name | Switch Board | Fixture | Power(W) | Current (A) | Wire | Breaker
|  |  | K44 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 01 |  | ESB3 | K34 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k38 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K32 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k46 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K30 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k36 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K23 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k29 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K25 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k27 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K21 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 180 | 1.0227 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  | C5 | 20 | 0.11364 | 2 x 1.5 rm BYM
[12 empty] | 140 | 0.79545 | 2 x 1.5 rm BYM + 1.5 BYA ECC
Circuit No 02 |  | SB1 | K2 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k1 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 02 |  | ESB4 | K41 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k7 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C6 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k5 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K43 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k12 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K45 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k14 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K47 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k3 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C7 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k9 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K49 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k13 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K51 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | c3 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K53 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  |  | 200 | 1.1364 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB |  |  |  | C8 | 20 | 0.11364 | 2 x 1.5 rm BYM
[12 empty] | 200 | 1.1364 | 2 x 1.5 rm BYM + 1.5 BYA ECC
Circuit No 03 |  | SB2 | k24 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k20 | 20 | 0.11364 | 2 x 1.5 rm BYM |  | Circuit No 03 |  | ESB2 | K37 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k33 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K28 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k31 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K19 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k17 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C4 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k18 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K11 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k26 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K4C1 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k35 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC
|  |  |  | 160 | 0.90909 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB
[8 empty] | Circuit No 04 |  | ESB1 | K15 | 20 | 0.11364 | 2 x 1.5 rm BYM
Circuit No 04 |  | SB4 | k55 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K16 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k54 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K6 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k52 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K8 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k39 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | C2 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k50 | 20 | 0.11364 | 2 x 1.5 rm BYM |  |  |  |  | K10 | 20 | 0.11364 | 2 x 1.5 rm BYM
|  |  | k48 | 20 | 0.11364 | 2 x 1.5 rm BYM | [5 empty] | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC
|  |  |  | 120 | 0.68182 | 2 x 1.5 rm BYM + 1.5 BYA ECC | 5A SP MCB

## Sheet6
| Calculation for Total Power of SDB Diragram | [8 empty] | 0.7 | 0.3 | 0.3
Calculation_of_Total_Power_ESDB
SDB | Load Type | Circuits &Sockets | Power (W) | SDB Load (W) | SDB Current (A) | Breaker of MDB
SDB(Floor Type I) | SB | CKT1 | 280
|  | CKT2 | 340 |  |  |  | SDB | Load Type | Circuits &Sockets | Power (W) | SDB Load (W) | SDB Current (A) | Breaker of MDB
|  | CKT3 | 300 |  |  |  | ESDB(Floor_type_I) | ESB | CKT1 | 80
|  | CKT4 | 120 | [5 empty] | CKT2 | 120
|  | CKT5 | 160 | [5 empty] | CKT3 | 220
|  | Total | 1200 | [5 empty] | Total | 420
| P Socket | P1 | 3000 |  |  |  |  | P Socket | P3 | 3000
|  | P2 | 3000 | [5 empty] | P4 | 3000
|  | Total | 6000 | [5 empty] | Total | 6000
| Q Socket | Q1 | 4000 |  |  |  |  | Q Socket | Q3 | 4000
|  | Total | 4000 | [5 empty] | Total | 4000
|  | Total(All) |  | 3840 | 21.81 | 25 A SP MCCB |  |  | Total(All) |  | 3294 | 18.71 | 25A SP MCCB
SDB(Floor Type II) | SB | CKT1 | 280 |  |  |  | ESDB(Floor_type_II) | ESB | CKT1 | 160
|  | CKT2 | 340 | [5 empty] | CKT2 | 120
|  | CKT3 | 300 | [5 empty] | CKT3 | 20
|  | CKT4 | 120 | [5 empty] | Total | 300
|  | CKT5 | 180 |  |  |  |  | P socket | P3 | 3000
|  | Total | 1220 | [5 empty] | P4 | 3000
| P Socket | P1 | 3000 | [5 empty] | Total | 6000
|  | P2 | 3000 |  |  |  |  | Q Socket | Q3 | 4000
|  | Total | 6000 | [5 empty] | Total | 4000
| Q Socket | Q1 | 4000 | [5 empty] | Total(All) |  | 3210 | 18.23 | 25A SP MCCB
|  | Total | 4000
|  | Total(All) |  | 3854 | 21.89 | 25 A SP MCCB | Lobby | ESB | CKT1 | 60
[9 empty] | CKT2 | 20
Lobby | SB | CKT1 | 80 | [5 empty] | CKT3 | 20
|  | CKT2 | 60 | [5 empty] | Total(All) |  | 70 | 0.39 | 5A SP MCCB
|  | CKT3 | 20
|  | CKT4 | 100 |  |  |  | Ground_Floor | ESB | CKT1 | 40
|  | Total | 160 | [5 empty] | CKT2 | 140
|  | Total(All) |  | 182 | 1.03 | 5 A SP MCCB |  |  | CKT3 | 200
[9 empty] | CKT4 | 180
Ground_Floor |  | CKT1 | 160 | [5 empty] | CKT5 | 160
|  | CKT2 | 40 | [5 empty] | CKT6 | 80
|  | CKT3 | 40 | [5 empty] | Total(All) |  | 560 | 3.18 | 5A SP MCCB
|  | CKT4 | 120
|  | CKT5 | 80 |  |  |  | Basement | ESB | CKT1 | 140
|  | CKT6 | 460 | [5 empty] | CKT2 | 200
|  | CKT7 | 20 | [5 empty] | CKT3 | 120
|  | Total(All) |  | 644 | 3.65 | 5 A SP MCCB |  |  | CKT4 | 120
[9 empty] | Total(All) |  | 406 | 2.3 | 5A SP MCCB
Basement |  | CKT1 | 180
|  | CKT2 | 200
|  | CKT3 | 160
|  | CKT4 | 120
|  | Total(All) |  | 462 | 2.625 | 5 A SP MCCB